ATTACHMENT 1

Generator Installation at Owens Valley VLBA Site

Statement of Work

- Scope of Work

  - Background

    - The NRAO has purchased a standby generator set and automatic transfer switch for its remote site at Owens Valley, CA

    - The new equipment will supply backup power to the entire site, replacing the existing backup power system which services part of the site

    - This equipment is expected to be delivered onsite in late spring or early summer

    - This bid is for the installation of this equipment and the removal of obsolete components as detailed in paragraphs 1.2 and 1.3

  - Installation

    - Both the generator set and automatic transfer switch shall be installed near the utility service transformer

Figure 1: Utility Transformer, side view

Figure 2: Utility Transformer, front view

    - Both the generator set and automatic transfer switch shall be bolted to a contractor provided concrete slab

    - The transfer switch shall be installed such that it will provide power to the entire facility

    - All new power cabling shall be buried in conduit

  - Removal

    - The existing automatic transfer switch shall be removed from service

Figure 3: Existing Transfer Switch

    - NRAO staff may choose to salvage some components from the automatic transfer switch prior to its removal

    - New power cabling shall be installed, in conduit, in place of the removed transfer switch

  - Cleanup

    - The contractor shall handle disposal of all waste generated by this project

    - The contractor shall handle disposal of the old transfer switch

- Bid package

  - All bid packages shall include the following:

    - A quote for the work described in paragraph 0

    - A timeline

      - The timeline shall identify:

        - The number of days that the VLBA site is without power

        - The number of days the bidder will be onsite

    - A statement of availability

      - This will identify the dates on which the contractor is available to perform the work described in paragraph 0
and/or
a statement that the contractor will be available provided with (x) weeks’ notice

- Documentation

  - The winning bidder shall provide the following additional documentation:

    - A construction drawing detailing the concrete pad(s) to be poured

    - A drawing/sketch showing the position of the generator set and transfer switch in relation to the existing transformer and building

    - A site specific safety plan

- Jobsite

  - Owens Valley

Figure 4: Jobsite Location

  - Site visit

    - Bidders will be allowed a site visit

    - All site visits must be scheduled at least two weeks in advance

    - Restrictions on number of visitors and building access may be imposed due to Covid concerns

    - Activities undertaken during visits shall be documented and approved by the NRAO Covid Management Team prior to travel.

    - Visitors will be required to provide and use appropriate PPE while onsite.

    - All work performed onsite shall comply with current State of California COVID policies

  - Directions: Take US 395 South from Bishop CA. to Big Pine CA. Take highway 168 east for 2 miles, turn left on Leighton Lane (at Zurich historical marker) follow paved road for 3.5 miles.  Turn right on gravel road. Follow signs to VLBA antenna

- New equipment

  - Caterpillar C7.1 PGABR Standby Generator Set

    - Standby generator set

    - Fuel type: diesel

    - ISO8528 nameplate: 125kW emergency/standby electrical service

    - 208Y/120 volt, 3-phase, 4-wire, 60hz

    - EPA emission certified for US stationary emergency use

    - Weather protective enclosure - white Sound Attenuated Level 1

    - Integral critical grade exhaust system

    - UL142 closed top double wall fuel tank base; 402 gallon capacity

    - Lockable fuel cap, fuel level gauge & alarms, sender, vents, reliefs

    - EMCP 4.2B electronic modular control panel

    - Modbus RTU communications, configurable accessory I/O, programmable logic control

    - Remote - programmable annunciation panel (supplied loose)

    - UL489 main circuit breaker 400 AF 3-pole LSI electronic100% rated

    - Low coolant level shutdown, low coolant temperature alarm

    - Cat - lead acid engine start battery set, cables, secure mounting tray

    - Charging alternator + multi rate 10A battery charger with NFPA alarms

    - Engine jacket water heater

    - Digital voltage regulator & excitation module

    - Fluid fill; engine oil, engine coolant, battery electrolyte (fuel not included)

    - One round trip provides startup assistance & owner training services

  - Automatic Transfer Switch

    - 208Y/120 volt, 3-phase, 4-wire, 60 hertz Service Ent Rated

    - 400 amp, 3-pole, open transition, contactor type

    - Contactor switching, open transition transfer

    - Non-bypass isolation

    - MX150 digital microprocessor control

    - MEXEG accessory group

    - NEMA 3R outdoor enclosure

- Requests for information

  - For any questions or clarifications, please contact Magdalene Romero (575-835-7200, mromero@nrao.edu)